# BARROW-IN-FURNESS BOROUGH COUNCIL

POLLUTION PREVENTION AND CONTROL ACT 1999

ENVIRONMENTAL PERMITTING (ENGLAND & WALES)  REGULATIONS 2007 (AS AMENDED)

Permit Ref. No.:			PPC/B/12

Date Permit Issued:		30th March 2006

Name and Address of Operator:	ASDA Stores Limited

ASDA House

Southbank

Great Wilson Street

Leeds

LS11 5AD

# Name and Address of Registered Office:	As above.

Name and Address of Permitted Installation:	ASDA Petrol Filling Station

Walney Road

Barrow-in-Furness

Cumbria

LA14 5UG

The above named company is permitted to operate an installation for the unloading of petrol into stationary storage tanks at the above service station within the boundary marked in red on the attached plan (PPC/B/12/A1), subject to compliance with the following conditions.  The service station has 1 petrol storage tank.

Conditions

1.	Vapours displaced by the delivery of petrol into storage installations at service stations shall be returned through a vapour tight connection line to the mobile container delivering the petrol.  Unloading operations may not take place unless the arrangements are in place and properly functioning, subject to conditions 3, 4 and 5.

2.	The operator shall implement the schedule of preventative maintenance provided in the additional information sent to the regulator on 9th December 2005.

3.	All reasonably practicable steps shall be taken to prevent uncontrolled leaks of vapour from vents, pipes and connectors from occurring. The regulator shall be advised without delay of the circumstances of such a vapour leak if there is likely to be an effect on the local community, and in all cases such a vapour leak shall be recorded in the log book required under condition 34. In this condition and in condition 4 a vapour leak means any leak of vapour excepting those which occur through the vent mentioned in condition 11 during potentially hazardous pressurisation.

4.	The operator shall advise the regulator of the corrective measures to be taken and the timescales over which they will be implemented in the event of a vapour leak described in condition 3.

5.	Instances of vapour lock shall be recorded in the log book and under the circumstances detailed in condition 3, be advised to the regulator.

6.	The procedures in conditions 2 to 5 inclusive shall be reviewed in light of any modifications which occur to the facilities.  The regulator shall be advised of any proposed alteration in operating procedures.

7.	The vapour collection systems shall be of a size and design, as approved by the regulator, to minimise vapour emission during the maximum petrol and vapour flow in accordance with conditions 1 and 8 (i.e. when most tank compartments are being simultaneously discharged).

8.	The number of tanker compartments being discharged simultaneously shall not exceed two including the diesel compartment.

9.	The connection points on the tank filling pipes and vapour return pipe shall be fitted with secure seals to reduce vapour leaks when not in active use.  If apertures are provided on storage tanks for the use of dipstick, these shall be securely sealed when not in active use.

10.	The fittings for delivery and vapour return pipes shall be different to prevent mis-connection.

11.	The petrol storage tank vent pipe shall be fitted with a pressure vacuum relief valve to minimise vapour loss during unloading and storage of petrol.  The pressure vacuum relief valve shall be sized and weighted to prevent vapour loss, except when the storage tanks are subject to potentially hazardous pressurisation.

12.	When connecting hoses prior to delivery, the vapour return hose shall be connected before any delivery hose.  The vapour return hose shall be connected by the road tanker end first, and then at the storage tank end.

13.	Adjacent to each vapour return connection point for the storage tank, there shall be a clearly legible and durable notice instructing "Connect vapour return line before off-loading" or similar wording.  The sign shall also refer to the maximum number of tanker compartments which may be unloaded simultaneously in accordance with condition 8.

14.	If dip testing of storage tanks or road tanker compartments is performed before delivery, the dip openings shall be securely sealed prior to the delivery taking place.

15.	Road tanker compartment dip testing shall not be performed whilst the vapour hose is connected.

16.	A competent person who has received appropriate training shall remain near the tanker and keep a constant watch on hoses and connections during unloading.

17.	All road tanker compartment vent and discharge valves shall be closed on completion of the delivery.

18.	On completion of unloading the vapour hose shall not be disconnected until the delivery hose has been discharged and disconnected.  The delivery hose shall be disconnected at the road tanker end first.  The vapour return hose shall be disconnected at the storage tank end first.

19.	All connection points shall be securely sealed after delivery.

20.	If the storage tanks or road tanker compartments are dipped after delivery the dip openings shall be securely sealed after dip testing.

21.	Manhole entry points to storage tanks shall be kept securely sealed except when maintenance and testing are being carried out which require entry to the tank.

22.	Petrol delivery and vapour return lines shall be tested in accordance with the schedule provided in the additional information received by the regulator on the 9th December 2005.

23.	Pressure vacuum relief valves on petrol storage tank vents shall be checked for correct functioning, including extraneous matter, seating and corrosion at least once every three years.

24. 	Vapours displaced by the filling of petrol into vehicle petrol tanks at this service station shall be recovered through the use of an open active vapour recovery system. Filling of vehicle petrol tanks shall not take place unless such a system is in place and fully functioning.

25. 	The vapour recovery system referred to in condition 24 shall be certified by the manufacturer to have a hydrocarbon capture efficiency of not less than 85%.

Equipment used shall be approved for use under the regulatory regimes of at least one European Union or European Free Trade Association country.

26. 	The vapour recovery equipment referred to in condition 24 shall be designed, installed and tested in accordance with the relevant British, European and international standards or national methods in place at the time that the equipment was installed.

27. 	The installation has in place an automatic monitoring system in accordance with condition 29.

28. 	Petrol delivery and vapour recovery systems for vehicle petrol tanks shall be tested in accordance with the manufacturer's specifications prior to commissioning and for:

• 	Vapour containment integrity at least once every three years, and always following substantial changes or significant events that lead to the removal or replacement of any of the components required to ensure the integrity of the containment system.

• 	Effectiveness of the vapour recovery system at least once every three years where an automatic monitoring system is in place.

This shall be undertaken by measuring the ratio of the volume of vapour recovered to liquid petrol dispensed i.e. vapour/petrol (V/P) ratio. The V/P ratio shall be at least 95% and, where the vapours are recovered into the fuel storage tank, not greater than 105% to avoid excessive pressure build up and consequent release through the pressure relief valves. The V/P ratio shall be determined by simulating the dispensing of petrol using measuring equipment approved for use in any European Union or European Free Trade Association country. The method to be used shall involve measuring the volume of air recovered with fuel flow simulated at the dispenser and read electronically using the approved measuring equipment. This provides the ratio of air recovered to liquid dispensed (air/liquid ratio) which should then be corrected to provide the V/P ratio using an appropriate factor to account for the difference in viscosity between petrol vapour and air (‘k-factor’).

29. 	The automatic monitoring system referred to in condition 27 shall:

• 	Automatically detect faults in the proper functioning of the petrol vapour recovery system including the automatic monitoring system itself and indicate faults to the operator. A fault shall be deemed to be present where continuous monitoring during filling of vehicle petrol tanks indicates that the V/P ratio (condition 28) averaged over the duration of filling has fallen below 85% or has exceeded 115% for ten consecutive filling operations. This only applies to filling operations of at least 20 seconds duration and where the rate of petrol dispensed reaches at least 25 litres per minute.

• 	Automatically cut off the flow of fuel on the faulty delivery system if the fault is not rectified within 1 week.

• 	Be approved for use under the regulatory regime of at least one European Union or European Free Trade Association country.

30. 	Operators shall be notified without delay if the results from any monitoring or tests mentioned in conditions 28, 29 or 30 identifies adverse results, vapour recovery equipment failure or leaks if there is likely to be an effect on the local community, The operator should advise the regulator of the corrective measures to be taken and the timescales over which they will be implemented.

31. 	Effective preventative maintenance shall be employed on all aspects of the installation including all plant, buildings and the equipment concerned with the control of emissions to air. Preventative maintenance for all vapour recovery systems shall be carried out in accordance with the manufacturer’s instructions

33. 	Spares and consumables needed shall be held on site, or should be available at short notice from guaranteed suppliers, so that plant breakdowns can be rectified rapidly.

34. 	The operator shall maintain a log book at the permitted installation incorporating details of all maintenance, examination and testing, inventory checking, installation and repair work carried out, along with details of training given to operating staff at the service station.

The log book shall also detail any suspected vapour leak together with action taken to deal with any leak, in accordance with conditions 3, 4 and 5.

35. 	Venting of the petrol vapour shall be through the vent pipes marked  ‘V’ on the attached plan reference PPC/B/12/A1.

10th November 2009

Signed:.................................................................	Date ................................

Chief Environmental Health Officer

EXPLANATORY NOTES

These notes do not form part of the Permit

This Permit is issued under Regulation 12 of the Environmental Permitting (England & Wales) Regulations 2007 (2007 Regulations) to operate an installation carrying out one or more of the activities listed in Part B to Schedule 1 of those Regulations, to the extent authorised by the Permit.

The Permit includes conditions that have to be complied with. It should be noted that aspects of the operation of the installation which are not regulated by those conditions, are subject to the Operator using the best available techniques (BAT) for preventing or, where that is not practical, reducing emissions from the installation.

Section 3(1) of the Regulations defines “BAT” as follows:

a. ‘available techniques’ means those techniques which have been developed on a scale which allows implementation in the relevant industrial sector, under economically and technically viable conditions, taking into consideration cost and advantages, whether or not the techniques are used or produced inside the United Kingdom, as long as they are reasonably accessible to the operator;

b. ‘best’ means, in relation to techniques, the most effective way of achieving a general high level of protection of the environment as a whole;

c. ‘techniques’ includes both technology used and the way in which the installation is designed, managed, operated and decommissioned.

1)	Responsibility under Workplace Health and Safety Legislation - This permit is given in relation to the requirements of Environmental Permitting Regulations 2007 and subordinate regulations.  It must not be taken to replace any responsibilities you may have under workplace health and safety legislation.

2) 	Other responsibilities - This permit, in that it regulates only air pollution matters, does not absolve you of the responsibility of any other statutory requirement, such as any need to obtain planning permission, hazardous substances consent or Building Regulations approval from the Council.  Discharge consents from the local sewerage undertaker or a waste disposal licence from the Environment Agency may still be required.

3) 	Enforcement and Offences - It is an offence to operate a prescribed activity without a current permit.  The operator will be liable to enforcement action where;

a)  a new activity (as defined within the Environmental Permitting (England & Wales) Regulations 2007) is carried on without a proper permit, and

b) any of the conditions of the permit are breached.

4) 	Subsistence Charge - An annual fee (subsistence charge) due on 1st April each year (currently chargeable per activity per annum but subject to change by statutory instrument) is payable to Barrow-in-Furness Borough Council.

5) 	Confidentiality - The Permit requires the Operator to provide information to Barrow-in-Furness Borough Council.  The Council will place the information onto the public registers in accordance with the requirements of the 2007 Regulations.  If the Operator considers that any information provided is commercially confidential, it may apply to the Council to have such information withheld from the register as provided in the 2007 Regulations.  To enable Barrow Borough Council to determine whether the information is commercially confidential, the Operator should clearly identify the information in question and should specify clear and precise reasons.

6) 	Variations to the permit - This Permit may be varied in the future. If at any time the activity or any aspect of the activity regulated by the following conditions changes such that the conditions no longer reflect the activity and require alteration, the Regulator should be contacted.

7) 	Surrender of the permit - Where an Operator intends to cease the operation of an installation (in whole or in part) the regulator should be informed in writing, such notification must include the information specified in regulation 24 of the 2007 Regulations.

8) 	Transfer of the permit or part of the permit - Before the Permit can be wholly or partially transferred to another person, a joint application to transfer the Permit has to be made by both the existing and proposed holders, in accordance with Regulation 21 of the 2007 Regulations.  A transfer will be allowed unless the Authority considers that the proposed holder will not be the person who will have control over the operation of the installation or will not ensure compliance with the conditions of the transferred Permit.

9) 	Appeal against permit conditions - Anyone who is aggrieved by the conditions attached to a Permit can appeal to the Secretary of State for the Environment, Food and Rural Affairs.  Appeals must be made in accordance with the requirements of Regulation 31 and Schedule 6 of the 2007 Regulations.

Appeals should be sent to the Secretary of State for the Environment, Food and Rural Affairs.  The address is as follows:-

The Planning Inspectorate

Environmental Appeals Administration

Room 4/12 - Eagle Wing

Temple Quay House

2 the Square

Temple Quay

Bristol

BS1 6PN

Please Note - an appeal bought under Section 27 paragraph (1) (c), (d) or (e) in relation to the conditions in a permit will not suspend the effect of the conditions appealed against; the conditions must still be complied with.

In determining an appeal against one or more conditions, the Act allows the Secretary of State in addition to quash any of the other conditions not subject to the appeal and to direct the regulator either to vary any of these other conditions or to add new conditions.

10) 	Contact Details - If you are required to contact the Environmental Protection Section of the Environmental Health Department at Barrow-in-Furness Borough Council please telephone 01229 876386 or 876372 during office hours and ask for Anne Pearson (Environmental Protection – Team Leader) or Graham Barker (Environmental Protection Technical Officer).

End of Explanatory Note